## Cooling Cost Method
|  | Climate Type | City *USER INPUT* | Data Center Type *USER INPUT* | IT Load (MW) *USER INPUT* | Electricity Rate ($/kWh) | Total Electricity Cost ($/year) | Load Factor (%) | Range (°C) | CoC | Tons | Evap (gpm) | Blowdown (gpm) | Drift (gpm) | Peak Makeup (gpm) | Peak Makeup (MGD) | Peak Annual Makeup (MGY) | Actual Annual Makeup (MGY) | Water Rate ($/1000 gal) | Total Water Cost ($/year)
|  | Cold and Dry | Denver | AI/ML Cluster | 100 | 0.13 | 4745000 | 80% | 15 | 4 | 28433.3239 | 426.4999 | 142.1666 | 4.265 | 572.9315 | 0.82502 | 301.1328 | 240.9062 | 4.9 | 1180440.5118
AI/ML Cluster | 50 | Hot and Wet | Miami | AI/ML Cluster | 100 | 0.12 | 4380000 | 60% | 20 | 3 | 28433.3239 | 568.6665 | 284.3332 | 5.6867 | 858.6864 | 1.2365 | 451.3256 | 270.7953 | 5.5 | 1489374.3531
Hyperscale Cloud | 100
| 150 | Hot and Dry | Phoenix | AI/ML Cluster | 100 | 0.13 | 4745000 | 60% | 15 | 3 | 28433.3239 | 426.4999 | 213.2499 | 4.265 | 644.0148 | 0.92738 | 338.4942 | 203.0965 | 3.5 | 710837.7595
80% | 200
60% | 250 | Moderate | San Diego | AI/ML Cluster | 100 | 0.3 | 10950000 | 60% | 20 | 3 | 28433.3239 | 568.6665 | 284.3332 | 5.6867 | 858.6864 | 1.2365 | 451.3256 | 270.7953 | 11.5 | 3114146.3748
300
| 350 | Cold and Wet | Seattle | AI/ML Cluster | 100 | 0.12 | 4380000 | 60% | 10 | 4 | 28433.3239 | 284.3332 | 94.7777 | 2.8433 | 381.9543 | 0.55001 | 200.7552 | 120.4531 | 5.5 | 662492.124
400
450
| 550 | Environmental Impacts
| 600 | City Name | Avg Temp (⁰C) | Avg Annual Precipitation (mm/year) | Grid Carbon Intensity (kgCO2/kWh) | Climate Adjusted Electricity (MWh/year) | Annual CO2 (metric tons) | Carbon Price ($/ metric ton) | Annual Carbon Cost ($) | Normalized Carbon Cost (Scale: 0-1) | Climate Adjusted Water Use (gallons/year) | Raw Water Stress Index | Calculated Water Stress Score (1=low, 5=high) | Sustainability Score | Monthly Precip | Total Impact
| 650 | [10 empty] | Stress
| 700 | [10 empty] | Ratio
|  | Denver | 10.233 | 390 | 0.499 | 12422 | 6198 | 48 | 297504 | 0.91 | 827820 | 2123 | 2 | 0.68513 | 30.747 | 5.365
|  | Miami | 24.181 | 1712 | 0.408 | 14196 | 5792 | 48 | 278016 | 0.84 | 946080 | 553 | 1 | 0.65205 | 120.622 | 3.26
|  | Phoenix | 21.508 | 183 | 0.454 | 14788 | 6714 | 48 | 322272 | 1 | 985500 | 5385 | 5 | 0.84719 | 16.231 | 11.5
|  | San Diego | 16.438 | 249 | 0.408 | 13013 | 5309 | 48 | 254832 | 0.76 | 867240 | 3483 | 3 | 0.61268 | 21.014 | 7.14
|  | Seattle | 11.103 | 945 | 0.091 | 10056 | 915 | 48 | 43920 | 0 | 670140 | 709 | 1 | 0.13457 | 76.224 | 2
Summary of Parameters
City — Identifies the geographic location so you can compare climate‑driven differences in water use.
IT Load (MW) — The total computing power that ultimately becomes heat the cooling system must reject. Input value in MW (e.g., PIT). This is assumed to be the same for each City.
Load Factor (%) — The average fraction of full IT load the data center runs at over time, used to scale annual water use. Two different IT loads are considred for this project: 60% for hyperscale cloud data centers and 80% for AI/ML cluster data cente.
Range (°F) — The temperature drop across the cooling tower (hot‑water return minus cold‑water supply), which directly sets evaporation. This assumes the allowable hot water return temperature is 70 °F. The cold-water supply will vary from 55 - 60 °F based on the average temperature of the City. We can use our judgement to estimate the cold-water supply temperature.
Cycles of Concentration (CoC) — How many times dissolved minerals are allowed to concentrate before blowdown occurs, which determines blowdown volume. This is a function of water quality and treatment practices. Hard water has lower CoC and soft water has higher CoC. The typical range is 3 - 5. We can use our judgement to estimate CoC.
Tons — The cooling capacity required, calculated from IT load, and used as the basis for evaporation estimates.
Evap (gpm) — The water lost to evaporation, which is the fundamental mechanism for heat rejection in a cooling tower.
Blowdown (gpm) — The water intentionally discharged to control mineral buildup, determined by evaporation and CoC.
Drift (gpm) — The small amount of water lost as droplets carried out of the tower exhaust air.
Makeup (gpm) — The total city‑water demand needed to replace evaporation, blowdown, and drift.
Makeup (MGD) — The daily volume of city water required to operate the cooling system at the specified load.
Annual Makeup (MGY) — The total yearly water consumption, scaled by load factor, used for water‑scarcity and sustainability analysis.

## Notes
Note - The Avg Annual Precip values were taken from the official 1991–2020 U.S. Climate Normals (NOAA), which are 30-year averages calculated from thousands of weather stations.